AOMS 65% review comments from Lt Rich Updike, 15 CES/CECP, Base Comprehensive Planner and Airfield Waiver Program Manager

- General Comments

  - NUMEROUS changes to this will occur with official adaptation of FAA Clearance Criteria with regards to the primary surface, since 8L Runway transfer.  Recommend this is resolved and incorporated into AOMS before delivery of final product.  All current obstructions/waivers will be placed in the Hickam AOMS database.  Once the FAA criteria is adopted 15th CES can move the appropriate obstructions from active to history.

  - Photograph names should be changed to reflect what the photo is.  Photo file names such as MVC-0101.jpg are not acceptable.

  - It’s almost a guarantee that HQ PACAF personnel will want to answer the question, “What within the waiver package has changed since the previous submission?”  They will not want to review the entire waiver package to note only the changes.  Recommend considering an automatic field that tracks data changes to a record and enters that modification date in the associated field.  That is, each record should have a field titled, “Date this record was last modified.”  Do not make it a user-entered value.

  - Recommend PACAF allow the first submission of the AOMS package to be a complete overhaul of the waiver/obstruction package from Hickam AFB.  This system vastly improves not only the presentation, but the accuracy of the report.  Request PACAF be understanding that many obstructions/exemptions/deviations/etc have existed for years at Hickam but were not adequately documented.  This system will allow adequate and complete documentation to occur.

- “Edit Obstructions” Comments

  - “Edit Obstructions” GENERAL Comments

- Request no data fields be limited by size.  Example: Field for Approval Authority…not enough character positions to type in Steven J. Redmann, Brigadier General, USAF.  We may have someday have an approving leader with name Abercrombie C.H. Bartholomew-Stoyanovich, III., PhD, AICP, Col, USAF

- I don’t agree with all the grouping methods.  For example, we show 3 records under “Waiver #1,” however, each of those records show multiple obstructions.  I think we should start this AOMS system with a clean-slate…meaning, each obstruction should have its own record even if there are six identical obstructions in a close proximity (i.e., light poles, etc.).  Record 1 should be light pole #1; Record 2 should be light pole #2.

- Missing Waiver #7, #10, #23, #25, #26, #35, and #42 entirely.  That’s because #7, #10, #25, and #35 became Permissible Deviations.  Should re-number or make some type of note about why they are missing.  #23, #26, and #42 are “Corrected” and should be noted accordingly.

- All fields need to automatically enter any new entry to their respective pull-down.  For example, if “Parking Apron” does not appear on the associated pull-down menu, it can be typed into the field and the system will automatically add it to the pull-down.

- Error message regarding photographs appear when attempting to advance from Record #18 to Record #19.

- Error message regarding photographs appear when attempting to advance from Record #57 to Record #58.

- Error message regarding photographs appear when attempting to advance from Record #67 to Record #68.

- Record #21, Waiver #12.  For the record, State DOT does not plan to remove bridge.  HAFB needs documentation from FAA/State DOT that they assume responsibility for that bridge causing death/damage to a potential accident in that area.

- Data is quite incomplete.  Many data entries could be entered before final delivery.

- Advancing through records quickly locks the system up.  For example, toggling from Record #1 to Record #6 quickly.

- Not enough input data for Records #59, #61, #62, and #63 to evaluate.

- It would be useful on the “Edit Obstruction” page to have a direct link to a map showing the location.  As I review some of these obstructions, I have to try to deduce the location of the obstruction from the photo, but a map or a button to the map highlighting the obstruction’s location would be useful.

- Record 81 and Record 82 are depicting the same functionality.  We sometimes use Jersey Barriers as Blast Deflectors.  I don’t believe we need two records for this “common obstruction.”

- I question the criteria (3000’ x 3000’) for Waiver #16, Record #25…we don’t apply this criteria to 4L and 4R…or we shouldn’t…not USAF “Primary Surface.”  May possibly be eliminated with recent land transfer.

- Records potentially “removed” by recent 8L Runway land transfer include:

    - Record #16, mention of Clear Zone

    - Record #17, mention of Clear Zone

    - Record #18, mention of Clear Zone

    - Record #19, mention of Clear Zone

    - Record #20, mention of Clear Zone

    - Record #21

    - Record #22, mention of Clear Zone

    - Record #23, mention of Taxiway Clearance and Primary Surface

    - Record #24

    - Record #25

    - Record #26

    - Record #27

    - Record #28

    - Record #29

    - Record #40

    - Record #41

    - Record #42

    - Record #43

    - Record #56

    - Record #59, mention of Clear Zone

    - Record #61, mention of Clear Zone

    - Record #64

    - Record #65

    - Record #66

    - Record #67

  - “Edit Obstructions; Obstruction Window”

    - Yes/No on “Correctable.”  As far as I’m concerned this is a useless field.  All waivers are correctable for a cost, either quantifiable or non-quantifiable.  Example, Base Ops complex:  Waivered, but correctable.  Can be corrected by eliminating a parking spot and moving double yellow line and taxi lines farther from facility.  The financial cost here is minimal, however, the mission cost is large.  Disagree –  Yes all waivers are “correctable”, but some do not pass the common logic test concerning mission needs and funds expenditure.  This identifier is necessary both at the MAJCOM and Air Staff level.

    - Priority drop-down (1,2,3).  Is this actually “Priority Area” 1, 2, or 3?…or a physical priority attached to order of removal?  If NOT “Priority Area,” eliminate drop down.  If it is “Priority Area,” it should be logically extracted by the software from the map.

    - Record #9, Waiver #4…add in fence even though it is slated to be removed in upcoming project.  Change Fuel Pit to non-classified.  Waiver is actually for the fence, not the fuel pit.

    - Non-classified…what about the tree behind the guardrail in photo for Record #66.  If violation…should be added.

    - AGL is Above Ground Level.  What is MSL?

    - Believe error on Record #38 and Record #39.  PACAF Form 48 shows Waiver P30 as being three obstructions, a debrief trailer, Bldg 3402, and Bldg 3404.  Records #38 and #39 show two obstructions assuming Bldgs 3402 and 3404 were both debrief trailers.  That is incorrect.  There are three obstructions; where exactly the debrief trailer is will have to be verified from the field.

    - Original Gov’t supplied Form 48 showed two line items to Waiver #40 (P40A and P40B).  One item (P40A) was an actual waiver for the wingtip violation created by the wash rack and is adequately identified in Record #54.  The other (P40B), however, is a permissible deviation to the apron clearance created by the wash rack; this deviation is not documented adequately as a “Deviation.”  Lastly, the “Transformer with Bollards” noted in Record #53 is an item that is actually “non-classified” as it was not the original waiver intent behind P40A.

  - “Edit Obstructions; Violations Window”

    - Add selection for “Wingtip Clearance” as a “Control Surface” and the associated “Actual Surface” will be “Parking Apron.”  This will, in turn, remove “Wingtip Clearance” from the “Actual Surface” pull-down.

    - Distances from criteria and violation distances need to be poised to automatically calculate based on GPS derived locations.  Can be manually entered in the interim, but need to eventually be automatic from ground survey data.

    - Distance from ______ is what?  Actual distance or required distance?  Appears to be “Required Distance.”  If Required distance, it should be a logical entry based on “Control Surface.”  Inconsistent; Record #4 shows Apron Distance 125’ (required distance) and Wingtip Clearance 135’ (actual distance; required is 162’).

    - Display units for Distance in “Violations” window (e.g., Distance (feet)).

    - Record #16, middle violation, Clear Zone.  Violation is NOT 125’.  Violation is directly on the threshold.  It either needs to be moved 3000’ west or 1’ east depending on how you look at “violation distance.”

    - “Violations” should have a field for “Actual Distance.”  For example, Record #23 shows the airfield fence being a 12’ violation to a 200’ criteria.  We should show that it is actually 188’ to Taxiway Centerline with an “Actual Distance” field.

    - Creating a link from the Violation specified to the actual regulation would be useful.  That is, when remarking that an obstruction is a permissible deviation, create a link from the data “Permissible Deviation; A14.2.15,” back to the actual AFI 32-1123 page showing that authorization as actually written.  The same goes for entries in the “Violations” window.

    - Record #23 also violates the 1000’ USAF Primary Surface Criteria for 8L/26R.  This violation is eliminated once FAA Criteria is adopted for the Primary Surface.

    - Taxiways “A” and “B” do not not meet USAF Criteria for separation from Primary Surface and yet have never been documented as such.  Again, this violation is eliminated once FAA Criteria is adopted for the Primary Surface.

    - Record #24, “Actual Surface” is more so a violation of 4L/22R but may still be a violation of 4R/22L.  This is possibly an elimination item due to the recent land transfer.

    - Record #25, “Actual Surface” is NOT 8L/26R, it is 4L and 4R.  This is possibly an elimination item due to the recent land transfer.

    - Record #64 is on land already transferred to State/FAA.  Function relocation is scheduled soon.

    - Record #71, “Control Surface” is NOT the “Clear Zone.”

  - “Edit Obstructions; Corrective Actions Window”

    - Fund sources on the related drop-down menu for obstruction removal are not useful to AF or Hickam AFB.  Need to eliminate the unneeded sources and add in our sources.  For example, MILCON is listed as MCAF (Military Construction Air Force)…needs to be changed to MILCON or Military Construction.  Fields need to be such that we can add new sources that don’t appear on the drop-down selection menu and they are automatically added to the drop-down.

    - “Corrective Actions” FIM category.  Believe should also show FIM area, BS-Base Support, MS-Mission Support, PM-Primary Mission, or CS-Community Support.

    - Corrective Actions data is programmed in ACES.  AOMS should be poised for eventually linking to ACES for this data instead of double entering this data in two databases.

    - Cost estimates are incorrect on Records #10, 11, and 12.  Should be $29M or  $29000K, not 100.

    - Many descriptions list AORP Matrix “X.”  This should actually be the Project Title, if I’m not mistaken.

    - A Corrective Action for Record #60 is to repaint the double-yellow apron edge.  Planned as part of new aircraft parking plan and FY02 DLA MILCON.

  - “Edit Obstructions; Installation Coordination Window”

    - What is the “Installation Coordination” window used for?  Approval is adequate.  Coordinations are done by the three additional names shown in “Approval” window (i.e., Steve Tullos, Col Razo, and LtCol Ward).

  - “Edit Obstructions; Approval Window”

    - Approval authority names will be the same regardless of the waiver (active waivers, exemptions, etc) and should only be entered once and carry over to display with all obstructions.

  - “Edit Obstructions; Media Window”

    - Photos should all be taken from the obstruction criteria to the obstruction as a standard (e.g., from Double Yellow apron line to subject obstruction) or from obstruction to criteria with obstruction appearing in photo.  Time of day is important when taking these photos to ensure proper light and no shading of obstruction.

    - Recommend pictures for ALL obstructions, not just show as “typical.”  For example, photos for all six light poles in Record #1.

    - Photo for Record #4, Waiver #2 is poor quality; doesn’t adequately depict violation.

    - Poor photo for Record #5, Waiver #3…again take photo from double-yellow to fence.

    - No photos for Records #14, #22, #27, #28, #32 #35, #36, #40, #41, #42, #53, #59 #61, #62, #63, #78, #83, #84.

- Map Comments

  - Alleviate the “bug” with color problems.  Zooming in makes entire map appear red.

- Report Writing Comments

  - Desire to see Form 48 Report Writing output.

  - Recommend creating a customized report writing mechanism such that user can create any report based on all fields currently existing.